## OT spec 2.3b
;Data-Id Map (OpenTherm Technical Specifications v2.3b)
;Remarks: This is a complete list of available defined ID's
; | it can be edited with a text editor. combined read/write ID's
; | are on 2 seperate lines. To reduce the number of lines
; | delete non used ID's
0 | STATUS | READ | FLAG | 0 | FLAG | 0 | Yes
1 | CONTROL SETPOINT | WRITE | F8.8 | 0 | 100 | 10 | Yes
2 | MASTER CONFIG/MEMBERID | WRITE | FLAG | 0 | U8 | 0 | 255 | 0 | Yes
3 | SLAVE CONFIG/MEMBERID | READ | FLAG | 0 | U8 | 0 | 255 | 0 | Yes
4 | COMMAND | WRITE | U8 | 0 | 255 | 2 | U8 | 0 | 255 | 0 | Yes
5 | FAULT FLAGS/CODE | READ | FLAG | 0 | U8 | 0 | 255 | 0 | Yes
6 | REMOTE PARAMETER SETTINGS | READ | FLAG | 0 | FLAG | 0 | Yes
7 | COOLING CONTROL | WRITE | F8.8 | 0 | 100 | 0 | Yes
8 | TsetCH2 | WRITE | F8.8 | 0 | 100 | 10 | Yes
9 | REMOTE ROOM SETPOINT | READ | F8.8 | -40 | 127 | 0 | Yes
10 | TSP NUMBER | READ | U8 | 0 | 255 | 0 | U8 | 0 | 0 | 0 | Yes
11 | TSP ENTRY | READ | U8 | 0 | 255 | 0 | U8 | 0 | 255 | 0 | Yes
11 | TSP ENTRY | WRITE | U8 | 0 | 255 | 0 | U8 | 0 | 255 | 0 | No
12 | FAULT BUFFER SIZE | READ | U8 | 0 | 255 | 0 | U8 | 0 | 0 | 0 | Yes
13 | FAULT BUFFER ENTRY | READ | U8 | 0 | 255 | 0 | U8 | 0 | 255 | 0 | Yes
14 | CAPACITY SETTING | WRITE | F8.8 | 0 | 100 | 0 | Yes
15 | MAX CAPACITY / MIN-MOD-LEVEL | READ | U8 | 0 | 255 | 0 | U8 | 0 | 100 | 0 | Yes
16 | ROOM SETPOINT | WRITE | F8.8 | -40 | 127 | 0 | Yes
17 | RELATIVE MODULATION LEVEL | READ | F8.8 | 0 | 100 | 0 | Yes
18 | CH WATER PRESSURE | READ | F8.8 | 0 | 5 | 0 | Yes
19 | DHW FLOW RATE | READ | F8.8 | 0 | 16 | 0 | Yes
20 | DAY - TIME | READ | U8 | 0 | 255 | 0 | U8 | 0 | 59 | 0 | Yes
20 | DAY - TIME | WRITE | U8 | 0 | 255 | 0 | U8 | 0 | 59 | 0 | No
21 | DATE | READ | U8 | 1 | 12 | 1 | U8 | 1 | 31 | 1 | Yes
21 | DATE | WRITE | U8 | 1 | 12 | 1 | U8 | 1 | 31 | 1 | No
22 | YEAR | READ | U16 | 1900 | 2099 | 2002 | Yes
22 | YEAR | WRITE | U16 | 1900 | 2099 | 2002 | No
23 | SECOND ROOM SETPOINT | WITE | F8.8 | -40 | 127 | 0 | Yes
24 | ROOM TEMPERATURE | WRITE | F8.8 | -40 | 127 | 20 | Yes
25 | BOILER WATER TEMP. | READ | F8.8 | -40 | 127 | 20 | Yes
26 | DHW TEMPERATURE | READ | F8.8 | -40 | 127 | 20 | Yes
27 | OUTSIDE TEMPERATURE | READ | F8.8 | -40 | 127 | 10 | Yes
28 | RETURN WATER TEMPERATURE | READ | F8.8 | -40 | 127 | 19 | Yes
29 | SOLAR STORAGE TEMPERATURE | READ | F8.8 | -40 | 127 | 0 | Yes
30 | SOLAR COLLECTOR TEMPERATURE | READ | F8.8 | -40 | 127 | 0 | Yes
31 | SECOND BOILER WATER TEMP. | READ | F8.8 | -40 | 127 | 20 | Yes
32 | SECOND DHW TEMPERATURE | READ | F8.8 | -40 | 127 | 20 | Yes
32 | EXHAUST TEMPERATURE | READ | S16 | -40 | 127 | 20 | Yes
48 | DHW SETPOINT BOUNDS | READ | S8 | 0 | 127 | 0 | S8 | 0 | 127 | 0 | Yes
49 | MAX CH SETPOINT BOUNDS | READ | S8 | 0 | 127 | 10 | S8 | 0 | 127 | 90 | Yes
50 | OTC HC-RATIO BOUNDS | READ | S8 | 0 | 40 | 0 | S8 | 0 | 40 | 0 | Yes
56 | DHW SETPOINT | READ | F8.8 | 0 | 127 | 10 | Yes
56 | DHW SETPOINT | WRITE | F8.8 | 0 | 127 | 10 | No
57 | MAX CH WATER SETPOINT | READ | F8.8 | 0 | 127 | 90 | Yes
57 | MAX CH WATER SETPOINT | WRITE | F8.8 | 0 | 127 | 90 | No
58 | OTC HEATCURVE RATIO | READ | F8.8 | 0 | 40 | 0 | Yes
58 | OTC HEATCURVE RATIO | WRITE | F8.8 | 0 | 40 | 0 | No
; New ID for ventilation/heat-recovery applications
70 | STATUS V/H | READ | FLAG | 0 | FLAG | 0 | Yes
71 | CONTROL SETPOINT V/H | WRITE | U8 | 0 | 100 | 0 | Yes
72 | FAULT FLAGS/CODE V/H | READ | FLAG | 0 | U8 | 0 | 255 | 0 | Yes
73 | DIAGNOSTIC CODE V/H | READ | U16 | 0 | 65000 | 0 | Yes
74 | CONFIG/MEMBERID V/H | READ | FLAG | 0 | U8 | 0 | 255 | 0 | Yes
75 | OPENTHERM VERSION V/H | READ | F8.8 | 0 | 127 | 2.32 | Yes
76 | VERSION & TYPE V/H | READ | U8 | 0 | 255 | 1 | U8 | 0 | 255 | 0 | Yes
77 | RELATIVE VENTILATION | READ | U8 | 0 | 255 | 0 | Yes
78 | RELATIVE HUMIDITY | READ | U8 | 0 | 255 | 0 | Yes
78 | RELATIVE HUMIDITY | WRITE | U8 | 0 | 255 | 0 | No
79 | CO2 LEVEL | READ | U16 | 0 | 10000 | 0 | Yes
79 | CO2 LEVEL | WRITE | U16 | 0 | 10000 | 0 | No
80 | SUPPLY INLET TEMPERATURE | READ | F8.8 | 0 | 127 | 0 | Yes
81 | SUPPLY OUTLET TEMPERATURE | READ | F8.8 | 0 | 127 | 0 | Yes
82 | EXHAUST INLET TEMPERATURE | READ | F8.8 | 0 | 127 | 0 | Yes
83 | EXHAUST OUTLET TEMPERATURE | READ | F8.8 | 0 | 127 | 0 | Yes
84 | ACTUAL EXHAUST FAN SPEED | READ | U16 | 0 | 10000 | 0 | Yes
85 | ACTUAL INLET FAN SPEED | READ | U16 | 0 | 10000 | 0 | Yes
86 | REMOTE PARAMETER SETTINGS V/H | READ | FLAG | 0 | FLAG | 0 | Yes
87 | NOMINAL VENTIALTION VALUE | READ | U8 | 0 | 255 | 0 | Yes
87 | NOMINAL VENTIALTION VALUE | WRITE | U8 | 0 | 255 | 0 | No
88 | TSP NUMBER V/H | READ | U8 | 0 | 255 | 0 | U8 | 0 | 0 | 0 | Yes
89 | TSP ENTRY V/H | READ | U8 | 0 | 255 | 0 | U8 | 0 | 255 | 0 | Yes
89 | TSP ENTRY V/H | WRITE | U8 | 0 | 255 | 0 | U8 | 0 | 255 | 0 | No
90 | FAULT BUFFER SIZE V/H | READ | U8 | 0 | 255 | 0 | U8 | 0 | 0 | 0 | Yes
91 | FAULT BUFFER ENTRY V/H | READ | U8 | 0 | 255 | 0 | U8 | 0 | 255 | 0 | Yes
115 | OEM DIAGNOSTIC CODE | READ | U16 | 0 | 65000 | 0 | Yes
116 | BURNER STARTS | READ | U16 | 0 | 65000 | 0 | Yes
116 | BURNER STARTS | WRITE | U16 | 0 | 65000 | 0 | No
117 | CH PUMP STATRS | READ | U16 | 0 | 65000 | 0 | Yes
117 | CH PUMP STATRS | WRITE | U16 | 0 | 65000 | 0 | No
118 | DHW PUMP/VALVE STARTS | READ | U16 | 0 | 65000 | 0 | Yes
118 | DHW PUMP/VALVE STARTS | WRITE | U16 | 0 | 65000 | 0 | No
119 | DHW BURNER STARTS | READ | U16 | 0 | 65000 | 0 | Yes
119 | DHW BURNER STARTS | WRITE | U16 | 0 | 65000 | 0 | No
120 | BURNER OPERATION HOURS | READ | U16 | 0 | 65000 | 0 | Yes
120 | BURNER OPERATION HOURS | WRITE | U16 | 0 | 65000 | 0 | No
121 | CH PUMP OPERATION HOURS | READ | U16 | 0 | 65000 | 0 | Yes
121 | CH PUMP OPERATION HOURS | WRITE | U16 | 0 | 65000 | 0 | No
122 | DHW PUMP/VALVE OPERATION HOURS | READ | U16 | 0 | 65000 | 0 | Yes
122 | DHW PUMP/VALVE OPERATION HOURS | WRITE | U16 | 0 | 65000 | 0 | No
123 | DHW BURNER HOURS | READ | U16 | 0 | 65000 | 0 | Yes
123 | DHW BURNER HOURS | WRITE | U16 | 0 | 65000 | 0 | No
124 | OPENTHERM VERSION MASTER | WRITE | F8.8 | 0 | 127 | 0 | Yes
125 | OPENTHERM VERSION SLAVE | READ | F8.8 | 0 | 127 | 0 | Yes
126 | MASTER VERSION & TYPE | WRITE | U8 | 0 | 255 | 0 | U8 | 0 | 255 | 0 | Yes
127 | SLAVE VERSION & TYPE | READ | U8 | 0 | 255 | 1 | U8 | 0 | 255 | 0 | Yes